## MDB-1
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
MDB-1 | IP54 | MCCB | 2500A-3p |  | 2×4×630/400 XLPE | [7 empty] | 1500 kVA / 13 kV Transformer
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 55.92 | 385.67 |  |  |  |  | 02
MDP/EX | 4×150/95 PVC | 125A-3p | 03 |  |  | 55.92 | 385.67 |  |  | 04 | 2000A-3p | 3×4×1000/500 PVC | Fixed AS-BUILT Load
|  |  | 05 |  |  |  |  | 55.92 | 385.67 | 06
SPARE |  | 20A-1p | 07 | [6 empty] | 08 | 20A-1p |  | SPARE
SPACE |  |  | 09 | [6 empty] | 10 |  |  | SPACE
SPACE |  |  | 11 | [6 empty] | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 441.59 |  | 441.59 |  | 441.59
|  | Amps Per Phase |  | 1912.4729 |  | 1912.4729 |  | 1912.4729
|  | Total Power (kVA) |  | 1324.77
Load | kVA (S × DF) | DF % | D.Load
Lighting
SPARE | 0 | 100 | 0
Motor
Fixed AS-BUILT Load | 1157 | 100 | 1157
Sub-panel
MDP/EX | 167.75 | 100 | 167.75
Cumulative Demand Load |  |  | 1324.75

## MDP-EX
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
MDP/EX | IP54 | MCCB | 125A-3p |  | 4×150/95 XLPE | [7 empty] | MDB-1
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 12.43 | 43.48 |  |  |  |  | 02
FIXED AS-Build Load | 4×16/16 PVC | 63A-3p | 03 |  |  | 12.43 | 43.48 |  |  | 04 | 63A-3p | 4×150/95 PVC | DP-X
|  |  | 05 |  |  |  |  | 12.43 | 43.48 | 06
SPARE |  | 20A-1p | 07 | [6 empty] | 08 |  |  | SPACE
SPACE |  |  | 09 | [6 empty] | 10 |  |  | SPACE
SPACE |  |  | 11 | [6 empty] | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 55.91 |  | 55.91 |  | 55.91
|  | Amps Per Phase |  | 242.1395 |  | 242.1395 |  | 242.1395
|  | Total Power (kVA) |  | 167.73
Load | kVA (S × DF) | DF % | D.Load
Other
FIXED AS-Build Load | 37.3 | 100 | 37.3
Sub-panel
DP-X | 130.45 | 100 | 130.45
Cumulative Demand Load |  |  | 167.75

## DP-X
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
DP-X | IP54 | MCB | 63A-3p |  | 4×150/95 XLPE | [7 empty] | MDP/EX
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 38.59 | 4.9 |  |  |  |  | 02
LPEX2 | 4×70/35 PVC | 13A-3p | 03 |  |  | 38.59 | 4.9 |  |  | 04 | 50A-3p | 4×70/35 PVC | DP-F
|  |  | 05 |  |  |  |  | 38.59 | 4.9 | 06
SPARE |  | 20A-1p | 07 | [6 empty] | 08 |  |  | SPACE
SPACE |  |  | 09 | [6 empty] | 10 |  |  | SPACE
SPACE |  |  | 11 | [6 empty] | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 43.49 |  | 43.49 |  | 43.49
|  | Amps Per Phase |  | 188.3499 |  | 188.3499 |  | 188.3499
|  | Total Power (kVA) |  | 130.47
Load | kVA (S × DF) | DF % | D.Load
Sub-panel
DP-F | 14.69 | 100 | 14.69
LPEX2 | 115.76 | 100 | 115.76
Cumulative Demand Load |  |  | 130.45

## LPEX2
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
LPEX2 | IP54 | MCB | 13A-3p |  | 4×70/35 XLPE | [7 empty] | DP-X
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 8.15 | 4.44 |  |  |  |  | 02
Feeder-7 | 4×6/6 XLPE | 40A-3p | 03 |  |  | 8.15 | 4.44 |  |  | 04 | 20A-3p | 4×1.5/1.5 XLPE | Feeder-8
|  |  | 05 |  |  |  |  | 8.15 | 4.44 | 06
|  |  | 07 | 4.07 | 4.07 |  |  |  |  | 08
Feeder-6 | 4×4/4 XLPE | 20A-3p | 09 |  |  | 4.07 | 4.07 |  |  | 10 | 20A-3p | 4×1.5/1.5 XLPE | Feeder-9
|  |  | 11 |  |  |  |  | 4.07 | 4.07 | 12
|  |  | 13 | 4.07 | 2.67 |  |  |  |  | 14
Feeder-10 | 4×1.5/1.5 XLPE | 20A-3p | 15 |  |  | 4.07 | 2.67 |  |  | 16 | 13A-3p | 4×1.5/1.5 PVC | Fixed AS-Built Load
|  |  | 17 |  |  |  |  | 4.07 | 2.67 | 18
Feeder-5 | 2×25/16 XLPE | 100A-1p | 19 | 22.22 | 11.11 |  |  |  |  | 20 | 50A-1p | 2×10/10 XLPE | Feeder-4
SPARE |  | 20A-1p | 21 | [6 empty] | 22 | 20A-1p |  | SPARE
SPACE |  |  | 23 | [6 empty] | 24 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 60.8 |  | 27.47 |  | 27.47
|  | Amps Per Phase |  | 263.3175 |  | 118.9693 |  | 118.9693
|  | Total Power (kVA) |  | 115.74
Load | kVA (S × DF) | DF % | D.Load
Motor
Fixed AS-Built Load | 8 | 100 | 8
Other
Feeder-10 | 12.22 | 100 | 12.22
Feeder-4 | 11.11 | 100 | 11.11
Feeder-5 | 22.22 | 100 | 22.22
Feeder-6 | 12.22 | 100 | 12.22
Feeder-7 | 24.44 | 100 | 24.44
Feeder-8 | 13.33 | 100 | 13.33
Feeder-9 | 12.22 | 100 | 12.22
Cumulative Demand Load |  |  | 115.76

## DP-F
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
DP-F | IP54 | MCB | 50A-3p |  | 4×70/35 XLPE | [7 empty] | DP-X
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 0.91 | 0.91 |  |  |  |  | 02
Sump Pump 1 w/ Soft Start | 4C1.5 + 1.5 PVC | 6A-3p | 03 |  |  | 0.91 | 0.91 |  |  | 04 | 6A-3p | 4×1.5/1.5 PVC | Sump Pump 2 w/ Soft Start
|  |  | 05 |  |  |  |  | 0.91 | 0.91 | 06
|  |  | 07 | [6 empty] | 08
Sump Pump 3 (Backup) w/ Soft Start | 4×1.5/1.5 PVC | 6A-3p | 09 | [6 empty] | 10 |  |  | Feeder-14
|  |  | 11 | [6 empty] | 12
Waterwall LED Lighting #1 | 2×35/25 PVC | 16A-1p | 13 | 3 | 2.67 |  |  |  |  | 14 | 16A-1p | 2×16/16 PVC | Waterwall LED Lighting #2
LED Bollards | 2×10/10 PVC | 6A-1p | 15 |  |  | 1 | 1 |  |  | 16 | 6A-1p | 2×16/16 PVC | Control System
Auxiliary / Socket @ DB-F | 2×2.5/2.5 PVC | 6A-1p | 17 |  |  |  |  | 1 | 0.33 | 18 | 6A-1p | 2×1.5/1.5 PVC | Filter Room Lighting
Filter Room Exhaust Fan #1 | 2×1.5/1.5 PVC | 6A-1p | 19 | 0.25 | [5 empty] | 20 | 20A-1p |  | SPARE
SPARE |  | 20A-1p | 21 | [6 empty] | 22 |  |  | SPACE
SPACE |  |  | 23 | [6 empty] | 24 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 7.74 |  | 3.82 |  | 3.15
|  | Amps Per Phase |  | 33.521 |  | 16.544 |  | 13.6423
|  | Total Power (kVA) |  | 14.71
Load | kVA (S × DF) | DF % | D.Load
Lighting
Control System | 1 | 100 | 1
Feeder-14 | 0 | 100 | 0
Filter Room Lighting | 0.33 | 100 | 0.33
LED Bollards | 1 | 100 | 1
Waterwall LED Lighting #1 | 3.33 | 90 | 3
Waterwall LED Lighting #2 | 3.33 | 80.2 | 2.67
Motor
Filter Room Exhaust Fan #1 | 0.25 | 100 | 0.25
Sump Pump 1 w/ Soft Start | 2.72 | 100 | 2.72
Sump Pump 2 w/ Soft Start | 2.72 | 100 | 2.72
Sump Pump 3 (Backup) w/ Soft Start | 2.72 | 0 | 0
Other
Auxiliary / Socket @ DB-F | 1 | 100 | 1
Cumulative Demand Load |  |  | 14.69