## MDB-1
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
MDB-1 | IP54 | MCCB | 2500A-3p |  | 2×4×630/400 XLPE | [7 empty] | 1500 kVA / 13 kV Transformer
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 20.33 | 385.67 |  |  |  |  | 02
MDP/EX | 4×150/95 PVC | 125A-3p | 03 |  |  | 20.33 | 385.67 |  |  | 04 | 2000A-3p | 3×4×1000/500 PVC | Fixed AS-BUILT Load
|  |  | 05 |  |  |  |  | 20.33 | 385.67 | 06
SPARE |  | 20A-1p | 07 | [6 empty] | 08 |  |  | SPACE
SPACE |  |  | 09 | [6 empty] | 10 |  |  | SPACE
SPACE |  |  | 11 | [6 empty] | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 406 |  | 406 |  | 406
|  | Amps Per Phase |  | 1758.3369 |  | 1758.3369 |  | 1758.3369
|  | Total Power (kVA) |  | 1218
Load | kVA | DF % | Demand kVA
Lighting
SPARE | 0 | 100 | 0
Motor
Fixed AS-BUILT Load | 1157 | 100 | 1157
Sub-panel
MDP/EX | 60.99 | 100 | 60.99
Cumulative Demand Load |  |  | 1217.99

## MDP-EX
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
MDP/EX | IP54 | MCCB | 125A-3p |  | 4×150/95 XLPE | [7 empty] | MDB-1
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 12.43 | 7.9 |  |  |  |  | 02
FIXED AS-Build Load | 4×16/16 PVC | 63A-3p | 03 |  |  | 12.43 | 7.9 |  |  | 04 | 80A-3p | 4×150/95 PVC | DP-X
|  |  | 05 |  |  |  |  | 12.43 | 7.9 | 06
SPARE |  | 20A-1p | 07 | [6 empty] | 08 |  |  | SPACE
SPACE |  |  | 09 | [6 empty] | 10 |  |  | SPACE
SPACE |  |  | 11 | [6 empty] | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 20.33 |  | 20.33 |  | 20.33
|  | Amps Per Phase |  | 88.0468 |  | 88.0468 |  | 88.0468
|  | Total Power (kVA) |  | 60.99
Load | kVA | DF % | Demand kVA
Other
FIXED AS-Build Load | 37.3 | 100 | 37.3
Sub-panel
DP-X | 23.69 | 100 | 23.69
Cumulative Demand Load |  |  | 60.99

## DP-X
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
DP-X | IP54 | MCCB | 80A-3p |  | 4×150/95 XLPE | [7 empty] | MDP/EX
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 2.67 | 5.23 |  |  |  |  | 02
LPEX2 | 4×70/35 PVC | 13A-3p | 03 |  |  | 2.67 | 5.23 |  |  | 04 | 50A-3p | 4×70/35 PVC | DP-F
|  |  | 05 |  |  |  |  | 2.67 | 5.23 | 06
SPARE |  | 20A-1p | 07 | [6 empty] | 08 |  |  | SPACE
SPACE |  |  | 09 | [6 empty] | 10 |  |  | SPACE
SPACE |  |  | 11 | [6 empty] | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 7.9 |  | 7.9 |  | 7.9
|  | Amps Per Phase |  | 34.2139 |  | 34.2139 |  | 34.2139
|  | Total Power (kVA) |  | 23.7
Load | kVA | DF % | Demand kVA
Sub-panel
DP-F | 15.69 | 100 | 15.69
LPEX2 | 8 | 100 | 8
Cumulative Demand Load |  |  | 23.69

## LPEX2
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [5 empty] | Source:
LPEX2 | IP54 | MCB | 13A-3p |  | 4×70/35 XLPE | [5 empty] | DP-X
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] | L3 [kVA] | No | CB | Conductor | Description
|  |  | 01 | 2.67 |  |  |  | 02 | 20A-1p |  | SPARE
Fixed AS-Built Load | 4×1.5/1.5 PVC | 13A-3p | 03 |  |  | 2.67 |  | 04 |  |  | SPACE
|  |  | 05 |  |  |  | 2.67 | 06 |  |  | SPACE
SPACE |  |  | 07 |  |  |  |  | 08 |  |  | SPACE
SPACE |  |  | 09 |  |  |  |  | 10 |  |  | SPACE
SPACE |  |  | 11 |  |  |  |  | 12 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 2.67 |  | 2.67 | 2.67
|  | Amps Per Phase |  | 11.5634 |  | 11.5634 | 11.5634
|  | Total Power (kVA) |  | 8.01
Load | kVA | DF % | Demand kVA
Motor
Fixed AS-Built Load | 8 | 100 | 8
Cumulative Demand Load |  |  | 8

## DP-F
Name: | IP Protection Rating: | Main CB type: | Main CB size: |  | Main Cable size: | [7 empty] | Source:
DP-F | IP54 | MCB | 50A-3p |  | 4×70/35 XLPE | [7 empty] | DP-X
Description | Conductor | CB | No | L1 [kVA] |  | L2 [kVA] |  | L3 [kVA] |  | No | CB | Conductor | Description
|  |  | 01 | 0.91 | 0.91 |  |  |  |  | 02
Sump Pump 1 w/ Soft Start | 4C1.5 + 1.5 PVC | 6A-3p | 03 |  |  | 0.91 | 0.91 |  |  | 04 | 6A-3p | 4×1.5/1.5 PVC | Sump Pump 2 w/ Soft Start
|  |  | 05 |  |  |  |  | 0.91 | 0.91 | 06
|  |  | 07 | 0.91 | 3.33 |  |  |  |  | 08 | 16A-1p | 2×35/25 PVC | Waterwall LED Lighting #1
Sump Pump 3 (Backup) w/ Soft Start | 4×1.5/1.5 PVC | 6A-3p | 09 |  |  | 0.91 | 3.33 |  |  | 10 | 16A-1p | 2×16/16 PVC | Waterwall LED Lighting #2
|  |  | 11 |  |  |  |  | 0.91 | 1 | 12 | 6A-1p | 2×10/10 PVC | LED Bollards
Control System | 2×16/16 PVC | 6A-1p | 13 | 1 | 1 |  |  |  |  | 14 | 6A-1p | 2×2.5/2.5 PVC | Auxiliary / Socket @ DB-F
Filter Room Lighting | 2×1.5/1.5 PVC | 6A-1p | 15 |  |  | 0.33 | 0.25 |  |  | 16 | 6A-1p | 2×1.5/1.5 PVC | Filter Room Exhaust Fan #1
|  |  | 17 | [6 empty] | 18 | 20A-1p |  | SPARE
Feeder-14 |  |  | 19 | [6 empty] | 20 | 20A-1p |  | SPARE
|  |  | 21 | [6 empty] | 22 |  |  | SPACE
SPACE |  |  | 23 | [6 empty] | 24 |  |  | SPACE
|  | Power Per Phase (kVA) |  | 8.06 |  | 6.64 |  | 3.73
|  | Amps Per Phase |  | 34.9069 |  | 28.757 |  | 16.1542
|  | Total Power (kVA) |  | 18.43
Load | kVA | DF % | Demand kVA
Lighting
Control System | 1 | 100 | 1
Feeder-14 | 0 | 100 | 0
Filter Room Lighting | 0.33 | 100 | 0.33
LED Bollards | 1 | 100 | 1
Waterwall LED Lighting #1 | 3.33 | 100 | 3.33
Waterwall LED Lighting #2 | 3.33 | 100 | 3.33
Motor
Filter Room Exhaust Fan #1 | 0.25 | 100 | 0.25
Sump Pump 1 w/ Soft Start | 2.72 | 100 | 2.72
Sump Pump 2 w/ Soft Start | 2.72 | 100 | 2.72
Sump Pump 3 (Backup) w/ Soft Start | 2.72 | 0 | 0
Other
Auxiliary / Socket @ DB-F | 1 | 100 | 1
Cumulative Demand Load |  |  | 15.68